### CURRENT TRANSFORMERS

#### 220kV Current Transformer

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 3 | Applicable standard | IEC 60044-1 (2003-02); IEC 60815 (2008-10); IEC 60071-1 (2011-03); IEC 60137 (2008-07); IEC 61869-1 (2007-10); IEC 61869-2 (2012-09); IEC 60060 (2010-11); IEC 60529 (2001-02); IEC 60296 (2012-02); IEC 60422 (2013-01); IEC 60028 (1925) |  |
| 4 | Type | Outdoor, single phase, oil-immersed, Top core, directly earthed |  |
| 5 | Rated voltage | 245 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7 | Impulse Voltage (1.2/50s) withstand | >1050 kVpeak |  |
| 8 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | >460 kVrms |  |
|  | - Secondary windings | >3 kVrms |  |
| 9 | Capability of withstanding over-current (uninterrupted mode) | >120% of rated primary current |  |
| 10 | Rated Transformation Ratios | 1200-2000-3000/1A |  |
| 11 | Rated Thermal withstand Current | > 50 kA |  |
| 12 | Rated duration of short-circuits | > 1s |  |
| 13 | Rated Dynamic Withstand Current | > 125 kA |  |
| 14 | Maximum Partial Discharge Level | Comply with IEC 61869-1 |  |
| 15 | Dielectric dissipation factor (tanδ) |  |  |
|  | - Un / 3 | Comply with IEC 61869-2 |  |
| 16 | Core Characteristics : Ratio, Rated Burden, Accuracy Class |  |  |
|  | -Core No. 1 | 800-1200-2000/1A 30VA - 5P20 |  |
|  | -Core No. 2 | 800-1200-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 800-1200-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 4 | 800-1200-2000/1A 30VA - 5P20 |  |
|  | -Core No. 5 | 800-1200-2000/1A 30VA - 5P20 |  |
| 17 | Temperature rise limit of windings | 650C |  |
| 18 | Minimum creepage distance | >25 mm/kV |  |
| 19 | Transforming current performed at Secondary winding | Yes |  |
| 20 | Static load-bearing capacity | Comply with IEC 60044-1 and IEC 61869-1 |  |
| 21 | The other specification shall comply with specification in Document No. 1819/QĐ-EVNNPT dated 16/9/2025 of EVNNPT | Yes |  |

#### 110kV Current Transformer

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer | Stated by Bidder |  |
| 2 | Country of Origin | Stated by Bidder |  |
| 3 | Ordering number | Stated by Bidder |  |
| 4 | General specification | Comply with specification in Volume 2: Technical document for substation |  |
| 5 | Applicable standard | IEC 61869-1, IEC 61869-2 or equivalent |  |
| 6 | Type | Outdoor, single phase, oil-immersed, Top core, directly earthed |  |
| 7 | Nominal voltage of system | 110kV |  |
| 8 | Maximum operating voltage | 123 kV |  |
| 9 | Rated frequency | 50 Hz |  |
| 10 | Impulse Voltage withstand (1.2/50s) | > 550 kVp |  |
| 11 | Power Frequency Voltage withstand, 50Hz, 1 min |  |  |
|  | - Primary windings | > 230 kVrms |  |
|  | - Secondary windings | >3 kVrms |  |
| 12 | Minimum clearance between phase and earth | 1.100mm |  |
| 13 | Rated primary current (Ipr) |  |  |
|  | Type 1 for Incoming bay, Bus transfer bay | 800-1200-1600-2000A |  |
|  | Type 2 for OLH bays | 400-800-1200A |  |
| 14 | Rated transformation ratios |  |  |
|  | Type 1 for Incoming bay, Bus transfer bay | 800-1200-1600-2000A |  |
|  | Type 2 for OLH bays | 400-800-1200A |  |
| 15 | Rated Thermal withstand Current (Ith) | > 31,5 kA |  |
| 16 | Rated duration of short-circuits | > 1s |  |
| 17 | Capability of withstanding over-current (uninterrupted mode) | >120% of rated primary current |  |
| 18 | Rated Dynamic Withstand Current | > 78,75 kA |  |
| 19 | Maximum Partial Discharge Level at highest system voltage | ≤ 10pC |  |
| 20 | Resistance of secondary windings | Stated by Bidder |  |
| 21 | Dielectric dissipation factor (tanδ) at 50Hz, measured on a complete CT |  |  |
|  | - Measured by the manufacturer at factory (routine test) | ≤ 0,5% |  |
|  | - Measured at site after finishing installation | ≤ 0,5% |  |
| 22 | Oil level indicator | Yes |  |
| 23 | Core Characteristics : Ratio, Rated Burden, Accuracy Class |  |  |
|  | Type 1 (Incoming bay, Bus transfer bay): |  |  |
|  | -Core No. 1 | 800-1200-1600-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 800-1200-1600-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 800-1200-1600-2000/1A 20VA - 5P20 |  |
|  | -Core No. 4 | 800-1200-1600-2000/1A 20VA - 5P20 |  |
|  | -Core No. 5 | 800-1200-1600-2000/1A 20VA - 5P20 |  |
|  | Type 2 (OHL bays): |  |  |
|  | -Core No. 1 | 400-800-1200/1A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 400-800-1200/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 400-800-1200/1A 20VA - 5P20 |  |
|  | -Core No. 4 | 400-800-1600/1A 20VA - 5P20 |  |
|  | -Core No. 5 | 400-800-1200/1A 20VA - 5P20 |  |
| 24 | Connection box | Made from aluminum/ aluminum alloy or stainless steel. Minimum protection class: IP55 |  |
| 25 | Transforming ratio performed at secondary windings | Yes |  |
| 26 | Total Weight | Stated by Bidder |  |
| 27 | Name plate | Comply with IEC 61869-1, IEC 61869-2 or equivalent |  |
| 28 | Support insulator: |  |  |
|  | - Applicable standard | IEC 62155 or equivalent |  |
|  | - Materials | Brown porcelain |  |
|  | - Minimum creepage distance | 25mm/kV |  |
|  | - Total creepage distance | Stated by Bidder |  |
|  | - Mechanical load-bearing capability | Stated by Bidder |  |
| 29 | Terminal connectors |  |  |
|  | - Manufacturer | Stated by Bidder |  |
|  | - Country of origin | Stated by Bidder |  |
|  | - Materials | Aluminum alloy |  |
|  | - Dimensions (quantity and size of holes) | Suitable for conductors/ busbar |  |
|  | - Quantity of terminal connectors per 1 CT | 2 |  |
|  | - Bolts and nuts | Stainless steel |  |
| 30 | Operation conditions | Suitable for conditions of project site |  |
| 31 | Technical documents | English/ Vietnamese; Comply with specification in Volume 2: Technical document for substation |  |
| 32 | Standard of quality management | ISO 9001:2008 or higher |  |
| 33 | Specification of testing | Comply with specification in Volume 2: Technical document for substation |  |
| 34 | Certificate of sample approval issued by STAMEQ | Yes |  |
| 35 | The other specification shall comply with specification in Document No. 105/QĐ-HĐTV dated 21/9/2021 of EVN | Yes |  |

#### 22kV Current Transformer

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture | Stated by Bidder |  |
| 2 | Country of Origin | Stated by Bidder |  |
| 3 | Ordering number | Stated by Bidder |  |
| 4 | Applicable standard | IEC 61869-1, IEC 61869-2, TCVN 11845-2, TCVN 7697-1 or equivalent |  |
| 5 | Type | Outdoor, Single phase, oil-immersed or cast resin (Epoxy Resin) type |  |
| 6 | Maximum operating voltage | 24 kV |  |
| 7 | Neutral system | Isolated |  |
| 8 | Rated frequency | 50 Hz |  |
| 9 | Rated Primary Current |  |  |
|  | - Type 1 | 50-100A |  |
|  | - Type 2 | 1200-2000A |  |
| 10 | Rated Secondary Current | 1A |  |
| 11 | Capability of withstanding over-current (uninterrupted mode) | >120% of rated primary current |  |
| 12 | Rated Thermal withstand Current (1s) | > 25 kA |  |
| 13 | Rated Dynamic Withstand Current | > 62,5 kA |  |
| 14 | Rated Transformation Ratios |  |  |
|  | - Type 1 | 50-100/1/1A |  |
|  | - Type 2 | 1200-2000/1 A |  |
| 15 | Core Characteristics : Ratio, Rated Burden, Accuracy Class |  |  |
|  | Type 1: |  |  |
|  | -Core No. 1 | 50-100/1-1A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 50-100/1A 20VA - 5P20 |  |
|  | Type 2 : |  |  |
|  | -Core No. 1 | 1200-2000/1A 20VA - 5P20 |  |
| 16 | Impulse Voltage withstand (1.2/50s) | > 125 kVpeak |  |
| 17 | Power Frequency Voltage withstand of Primary winding | > 50 kVrms |  |
| 18 | Power Frequency Voltage withstand of Secondary windings | >3 kVrms |  |
| 19 | Maximum Partial Discharge Level at 1,2Um/ 3 |  |  |
|  | Cast resin | 20 pC |  |
|  | Oil-immersed | 5 pC |  |
| 20 | Temperature rise limit | 600C |  |
| 21 | Minimum creepage distance | >25 mm/kV |  |
| 22 | Oil level indicator, oil-draining valve (for oil-immersed type) | Yes |  |
| 23 | Connection box and lead-sealing position | - Lid of connection box shall be made from aluminum, aluminum alloy, stainless steel or hot-dip galvanized plate steel. - Lid or bottom and bolts of lid associated with holes for lead-sealing. |  |
| 24 | Label of terminals | Label of terminals shall clearly indicate: - Primary and secondary windings; - Parts of windings (if any); - Associated poles of windings and parts of windings; - Intermediate steps (if any). Terminals shall be so clearly marked to be easy detected outside or at vicinity. Label writing shall be performed as follow: - Letters shall be placed after or before numbers, and be capital. - Marks of terminals shall comply with TCVN or relevant IEC standards. |  |
| 25 | Nameplate of CT | Nameplate shall be fixed on CT, and at least contain the followings: - Name of the manufacturer or other signals indicating the manufacturer; - Code and serial number; - Year of manufacturing; - Rated current of primary and secondary windings; - Rated frequency; - Rated power and accuracy; - Highest voltage of CT; - Rated insulation level; - Thermal withstand (Ith) and dynamic withstand current (Idyn); - Insulation class (in case of other than class A). All above information shall not be faded over the years of operation period. |  |
| 26 | Accessories | - Terminals and Terminal connectors at medium voltage shall be made from brass or nickel plated copper to be suitable for designed copper/ aluminum conductor. - CT with rated current of up to 150-300A: Using terminals to connecting with conductors. - CT with rated current of up to 200-400A: Using flat connectors to connect with compressed cosse. - Bottom details and bolts shall be hot-dip galvanized or stainless steel. |  |
| 27 | The other specification shall comply with specification of Document No. 105/QĐ-HĐTV dated 21/9/2021 of EVN | Yes |  |

### CAPACITOR Voltage Transformers

#### 220kV Capacitor Voltage Transformers

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/ Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013) |  |
| 4 | Type | Outdoor, single phase, oil immersed, directly earthed neutral |  |
| 5 | Rated voltage | 245 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7 | Impulse Voltage withstand (1.2/50s) | > 1050 kV |  |
| 8 | Power Frequency Voltage withstand at 50Hz, 1 min |  |  |
|  | - Primary windings | >460 kV |  |
|  | - Secondary windings | >3 kV |  |
| 9 | Rated voltage factor and rated time: | 1,2 (continuous) |  |
|  |  | 1,5 (30 seconds) |  |
| 10 | Static load-bearing capability (FR) of high voltage terminal | ≥ 1250 N |  |
| 11 | Insulators | Brown porcelain |  |
| 12 | Minimum creepage distance | > 25 mm/kV |  |
| 13 | Voltage ratio, burden, accuracy class |  |  |
|  | + Winding No.1 | 220kV:√3/110V:√3; 25VA; class 0.5 |  |
|  | + Winding No.2 | 220kV:√3/110V:√3; 50VA; 3P |  |
| 14 | Temperature rise limit of winding | 650C |  |
| 15 | The other specification shall comply with specification in Document No. 1816/QĐ-EVNNPT dated 16/9/2025 of EVNNPT | Yes |  |

#### 110kV Capacitor Voltage Transformers

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer | Stated by Bidder |  |
| 2 | Country of Origin | Stated by Bidder |  |
| 3 | Ordering number | Stated by Bidder |  |
| 4 | General specification | Comply with specification in Volume 2: Technical document for substation |  |
| 5 | Applicable standard | IEC 61869-1, IEC 61869-5 or equivalent |  |
| 6 | Type | Outdoor, single phase, capacitor type, oil immersed, directly earthed neutral |  |
| 7 | Support insulator | One piece, no joints |  |
| 8 | Nominal voltage of system | 110kV |  |
| 9 | Maximum operating voltage | 123 kV |  |
| 10 | Rated frequency | 50 Hz |  |
| 11 | Impulse Voltage withstand (1.2/50s) | > 550 kVpeak |  |
| 12 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | >230 kVrms |  |
|  | - Secondary windings | >3 kVrms |  |
| 13 | Minimum phase – earth clearance | 1.100mm |  |
| 14 | Rated voltage factor and rated time: | 1,2 (continuous) |  |
|  |  | 1,5 (30 seconds) |  |
| 15 | Rated capacitance (pF) | Stated by Bidder |  |
| 16 | Guaranteed limit of Rated capacitance (%) | Stated by Bidder |  |
| 17 | Maximum Partial Discharge Level at highest system voltage | ≤ 10pC |  |
| 18 | Flux Density at Rated Voltage (Tesla) | Stated by Bidder |  |
| 19 | Tanδ at 50Hz frequency: |  |  |
| 19.1 | Result of Routine test performed by the manufacturer at its factory, conducted on completed CVT, voltage divider capacitor set, EMU unit: |  |  |
|  | Voltage divider capacitor set | ≤ 0,5% |  |
|  | EMU unit | Stated by Bidder |  |
|  | Completed CVT | ≤ 1% |  |
| 19.2 | After completely installing at site | ≤ 1% |  |
| 20 | Voltage ratio, burden and accuracy class |  |  |
|  | + Winding No.1 | 110kV:√3/110V:√3; 15VA; class 0.5 |  |
|  | + Winding No.2 | 110kV:√3/110V:√3; 15VA; class 0.5 |  |
|  | + Winding No.3 | 110kV:√3/110V:√3; 50VA; class 3P |  |
| 21 | Materials of connection box | Aluminum/ Aluminum alloy/ stainless steel; IP55 protection level |  |
| 22 | Oil level indicator and draining valve | Yes |  |
| 23 | Name plate | Comply with IEC 61869-1, IEC 61869-5 or equivalent |  |
| 24 | Total weight | Stated by Bidder |  |
| 25 | Support insulator |  |  |
| 25.1 | Applicable standard | IEC 62155 or equivalent |  |
| 25.2 | Materials | Brown porcelain |  |
| 25.3 | Minimum creepage distance | 25 mm/kV |  |
| 22.2 | Total creepage distance (kN) | Stated by Bidder |  |
| 25.5 | Rated Mechanical Terminal Load | Stated by Bidder |  |
| 26 | Terminal connector |  |  |
| 26.1 | Manufacturer | Stated by Bidder |  |
| 26.1 | Country of origin | Stated by Bidder |  |
| 26.2 | Materials | Aluminum alloy |  |
| 26.3 | Dimensions (quantity of holes, size of hole…) | Suitable for terminals of CVT and connecting conductor |  |
| 26.4 | Quantity per one CVT (pcs) | 01 |  |
| 26.5 | Bolts and nuts | Stainless steel |  |
| 27 | Operation condition | Suitable for condition of project site |  |
| 28 | Technical documents | Comply with specification in Volume 2: Technical document for substation |  |
| 29 | Quality management standard | ISO 9001: 2008 or higher |  |
| 30 | Type tests | Comply with specification in Volume 2: Technical document for substation |  |
| 31 | Certificate of sample approval issued by STAMEQ | Yes |  |
| 32 | The other specification shall comply with specification in Document No. 104/QĐ-HĐTV dated 21/9/2021 of EVN | Yes |  |

#### 22kV Voltage Transformers

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture | Stated by Bidder |  |
| 2 | Country of Origin | Stated by Bidder |  |
| 3 | Ordering number | Stated by Bidder |  |
| 4 | Applicable standard | IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent |  |
| 5 | Type | Outdoor, single phase, 1 or 2 support insulator, inductive voltage transformer, oil immersed or epoxy resin |  |
| 6 | Highest operating voltage | 24 kV |  |
| 7 | Rated voltage at primary side | 22/3 kV |  |
| 8 | Rated voltage at secondary side | 110/3 V |  |
| 9 | Neutral type | Isolated |  |
| 10 | Rated frequency | 50 Hz |  |
| 11 | Quantity of secondary windings | 3 cores |  |
| 12 | Voltage ratio, burden, accuracy class |  |  |
|  | + Winding No.1 | 22kV:√3/110V:√3; 15VA; class 0.5 |  |
|  | + Winding No.2 | 22kV:√3/110V:√3; 25VA; 3P |  |
|  | + Winding No.3 | 22kV:√3/110V:3; 25VA; 6P |  |
| 13 | Impulse Voltage withstand (1.2/50s) | > 125 kVpeak |  |
| 14 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | > 50 kVrms |  |
|  | - Secondary windings | >3 kVrms |  |
| 15 | Rated voltage factor and rated time: | 1,2 (continuous) |  |
|  |  | 1,9 (8 hours) |  |
| 16 | Maximum Partial Discharge Level at 1,2Um/ 3 |  |  |
|  | Cast resin | 20 pC |  |
|  | Oil immersed | 5 pC |  |
| 17 | Temperature rise limit | 600C |  |
| 18 | Minimum creepage distance | >25 mm/kV |  |
| 19 | Oil level indicator and oil draining valve (for oil-immersed type) | Yes |  |
| 20 | Lid of secondary connection box and lead-sealing position | - Lid of secondary connection box shall be made from aluminum, aluminum alloy, stainless steel or hot-dip galvanized plate steel. - Lid or bottom of box and bolts of lid include holes for lead-sealing. |  |
| 21 | Label of terminals | Label of terminals shall clearly indicate: - Primary and secondary windings; - Parts of windings (if any); - Associated poles of windings and parts of windings; - Intermediate steps (if any). Terminals shall be so clearly marked to be easy detected outside or at vicinity. Label writing shall be performed as follow: - Letters shall be placed after or before numbers, and be capital. - Marks of terminals shall comply with TCVN or relevant IEC standards. |  |
| 22 | Nameplate of CT | Nameplate shall be fixed on CT, and at least contain the followings: - Name of the manufacturer or other signals indicating the manufacturer; - Code and serial number; - Year of manufacturing; - Rated voltage of primary and secondary windings; - Rated frequency; - Rated power and accuracy; - Highest voltage of VT; - Rated insulation level; - Rated voltage factor over operation time; - Insulation class (in case of other than class A). All above information shall not be faded over the years of operation period. |  |
| 23 | Accessories | - Terminals and Terminal connectors at medium voltage shall be made from brass or nickel plated copper to be suitable for designed copper/ aluminum conductor. - Bottom details and bolts shall be hot-dip galvanized or stainless steel. |  |
| 21 | The other specification shall comply with specification in Document No. 104/QĐ-HĐTV dated 21/9/2021 of EVN | Yes |  |